Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone (734) 615-7168  Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance .  This document is to be used in conjunction with the manufacturer's pre-start check list.

Project Name:

Project Number:

Completed by/representing (print):

# Air Cooled Chiller

Tag No. 			Model No. 				Serial No.

Check		Item					Comments

General Requirements

Equipment and components match reviewed and approved shop drawings

Installation instructions and drawings were reviewed during installation

Equipment and components are free of obvious physical damage

Equipment and surrounding area is clean

Nameplate data has been recorded, nameplate is attached and legible

Manufacturer's pre-start requirements have been reviewed and completed

Refrigeration Form has been completed and submitted to A/C Shop (Frank Hilberer)

CHW load has been established through weather or false loading to accommodate start-up

Coordination - the following must be notified of chiller start-up and be in attendance

Mechanical Contractor

Controls contractor

Electrical Contractor

Manufacturer's representative.

U of M DDC technician

U of M commissioner

U of M A/ C Shop

Start-up will be conducted by:

Installation Requirements

Chiller is set in place and ready

Shipping restraints have been removed

Properly supported and level

Vibration isolators have been adjusted and are free floating

Condenser coils have been raked

Condenser fans rotate freely by hand with no obstruction

Compressor and fan lubrication requirements have been checked and addressed

Action:

Refrigerant requirements have been checked and addressed

Unit was shipped with complete running charge

Action:

# Air Cooled Chiller Pre-Start Checklist

Chilled Water piping complete and ready

Piping,  valves, accessories installed per detail and manufacturer's instructions

Chilled water pumps have been successfully started

Piping is flushed, cleaned,  filled

Preliminary Hydronic System Start-up Report has been completed

Preliminary test and balance has been completed to ensure adequate flow through chiller.

All chilled water piping has been insulated, with continuous vapor barrier

Power wiring complete and ready

Terminations complete up to unit control panel

Unit protection requirements have been checked against that installed
		Action:

Controls complete and ready

Chiller control power is installed and ready

Unit mounted control transformer from primary power

Separate 120V circuit for controls

Terminations complete at DDC panel

DDC panel ready to generate/ receive DDC I/O

Terminations complete at chiller control panel

Field installed devices installed and wired per control and manufacturer requirements

Action:

Additional requirements have been completed

Additional Comments:

Certification:  I certify the above checks have been made and unit is ready for start-up  (signed/date)