CHECK-TEST-START-UP/FUNCTIONAL TEST

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone (734) 615-7168  Fax (734) 936-3334

Project Name:________________________________________________________________________

Project Number: ______________________________________________________________________

Start-up Date:_________________________

Attendees:

1) _________________________________________     2)____________________________________

3) _________________________________________     4)____________________________________

5) _________________________________________     6)____________________________________

7) _________________________________________     8)____________________________________

Cooling Towers

Induced Draft, Cross Flow, Direct Drive

Note- basis is Marley I,O,&M instructions.

System:   ________________________________________________

Notice: This is not a punch list.  Check-off indicates system is in general compliance and is ready for functional testing.  Punch listing is performed by the engineer of record, not the commissioning team.

Is system operating or is this initial start-up?_________________________________________________

Equipment			Specified/Approved			Verified

Model				________________________		_______	______________

No. of Cells			________________________

Motor HP/volts/			________________________		_______	______________

Amps				________________________

Motor Out Air			________________________		_______	______________

FM Approved			________________________		_______	______________

Inlet Air Screens			________________________		_______	______________

SS HW Basin			________________________		_______	______________

Basin Covers			________________________		_______	______________

2 pc. Float Valve			________________________		_______	______________

Vibration Switch			________________________		_______	______________

Plenum Walk Way		________________________		_______	______________

Inlet Screens			________________________		_______	______________

Fan Guard/ Screen							_____________________

Hand Rail			________________________		_______	______________

ladder			________________________		_______	______________

ladder cage		________________________		_______	______________

ladder extension		________________________		_______	______________

Basin Heaters (Y/N)		________________________		_______	______________

Qty.			________________________		_______	______________

Temp Probe		________________________		_______	______________

Low Water Cut-Out	________________________		_______	______________

Flumes				________________________		_______	______________

Equalizer Pipe			________________________		_______	______________

Flow Control (balancing)Valves	________________________		_______	______________

System Piped Per Design Drawings

Isolation valves: ________________________ Control Valves___________________________________

Drains _______________________________________________________________________________

Equalizer __________________ Overflow __________________________________________________

Make-Up Water ________________________________________________________________________

Specific Components

Flow Control Valves

Valve Stem Lubricated __________________________________________________________

Threads Coated w/Lube___________________________________________________________

Vibration Eliminators

No Misalignment _________ No Short Circuits -____________________________________________

Travel limit stops released, 1/4"-1/2" gap between washer and plate ______________________________

Drive Shaft/Gear Reducer

Check for obvious problems, alignment, balancing, and proper connection are factory rep.s responsibility.

Aligned ________	Balancing Bolts _______  Connection Bolts ___________________________

Verify Gear Reducer Lube Level_________________ Hand Rotation Test _______________________

Motors:

Re-greased per factory recommendations? ___________________________________________________

(ball brg. motors)

General Installation:

Cleaned:  HW Basin_________  CW Basin _________ Depressed Sump __________

Equalizer_____________________________________________________________________

Piping Adequately Supported______________________________________________________________

Tower/tower support are level _____________________________________________________________

FUNCTIONAL TESTS

Has Tower been water balanced?___________________________________________________________

Test is with tower under cooling load? _____________________________________________________

Basin Heater (tests must be performed with water in basin, heaters fully submerged.)

T-Probe > 6" from heater? ___________ T-Probe 1" or more above highest heater element___________

Element supports___________ (unsupported length to be ( 30")

Cycle Test (cool temp probe, witness heater cycling) ___________________________________________

Measure current and voltage at each heater phase while heater in operation:

Cell 1		    Cell 2		    Cell 3		       Cell 4

Voltage	 		___/___/____	___/___/____	___/___/____	___/_____/____

Amps	 		___/___/____	___/___/____	___/___/____	___/_____/____

Variation in phase to phase amp readings of more than a few percent indicates probable defective heater.

Low Water Cut-Out Test_________________________________________________________________

continued next page

Cooling Towers

Float Valve

No Snagging  ___________________________________________________________________

Correct Level Maintained__________________________________________________________

Cell 1		   Cell 2		   Cell 3		    Cell 4

Correct Rotation 		__________	__________	__________	____________

Measured Amps

(L1/L2/L3)		___/___/____	___/___/____	___/___/____	___/_____/____

Quiet Through-out	__________	__________	__________	____________

Speed Range

Vibe Switch		__________	__________	__________	____________

No Cold Basin Vortex	__________	__________	__________	____________

Even Water Distribution 	__________	__________	__________	____________

Across Hot Decks

List of other issues ___________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________