Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone (734) 615-7168  Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance .  This document is to be used in conjunction with the manufacturer's pre-start check list.

Project Name:

Project Number:

Completed by/representing (print):

# Electric Condensate Pumps

Tag No. 			Model No. 				Serial No.

Check		Item

Flushing complete, strainers cleaned

Receiver level and adequately supported

Vent pipe is same size as receiver vent connection

All horizontal vent pipe pitched back to receiver.  No traps in vent line

Condensate line pitched to receiver

Overflow loop installed

Overflow loop primer valve or capped "primer" nipple installed

Float shipping restraints removed, floats "free" and properly adjusted

No pipe weight or torque on pump flanges, pipe connections to pump not sprung in place

Pump and control panel data label info matches approved submittal

Pump/motor, tank, and control panel data labels secure, legible and undamaged

Valve installed between receiver and each pump inlet

Plug or balance valve located on pump discharge

Installed:  		Gage Glass 	    Thermometers		Pressure Gages

Check valves on discharge of each pump

Unions or flanges at strainer and at each pump

Wiring connections tight

Overflow loop primed

Receiver primed

Gage glass clear and tank water level visible

Pump off/rotate by hand/no drag

Pump rotation verified

List of other issues ___________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

After priming receiver and verifying pump rotations, operate pumps and verify correct float operation, lead lag operation, and all control panel functions, in advance of the Functional Testing that is to be witnessed by the UM Cx. agent.

Certification:  I certify the above checks have been made (signed/date)