Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone: (734) 615-7168   Fax: (734) 936-3334

Note- this document is rough and needs further review and refinement. DK 12-7-99.

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance.  This document is to be used in conjunction with the manufacturer's pre-start check list.

Project Name:

Project Number:

Completed by/representing (print):

Hot Water Heating Systems

Provide indentifying information for the folowing equipment, as applicable: heat exchangers, expansion tanks, air separators,

Tag No. 			Model No. 				Serial No.

At least two weeks prior to start-up

_____ Equipment installation manuals have been submitted to UM Cx

_____ The controls contractor generated "Commissioning Manual" (functional test procedure) has been submitted to the UM Cx

At least one week prior to start-up

_____ Equipment/System Start-up Notification Form has been faxed to the UM Cx agent

System Piped Per Design Drawings and Code

_____ Make-up

_____ HWH Piping

_____ Steam Piping

_____ Equipment is installed in strict compliance with design documenst/specification and per manufacturers installation instructions.

Flush, Clean, and Fill

_____System water piping has been flushed and cleaned

_____System steam and condnesate piping has been flushed and cleaned

_____Strainers clean, steam side

_____Strainers clean, HHW Side

_____System piping has been filled and properly vented

Heat Exchanger:

_____No pipe weight, torque, or mis-alignment on flanges

_____Adequate support for HX

_____If bolted to floor, feet or bracket mounting bolts loose to allow expansion

_____Room for tube pull

_____Data plate readable and not concealed (by insulation, etc.)

_____ Relief Valve(s) installed

_____ Relief Valve capacities checked against HX nameplate and approved submittal

_____ Relief Valve Discharge piped per design documents and Code

Vacuum Breakers

_____Installed on each HX

_____Bottom adjustment nut adjusted high on threads so vent operates under low vacuum condition?

(if nut is low on threads vent will not open until high vacuum occurs, effecting HX modulation)

_____Top jam nut tight against bottom adjustment nut?

PRV/City Water Makeup

_____Bypass closed

_____PRV set?

Setting ______________  PSIG

_____Gage Reading (downstream side of PRV)__________________ PSIG

System is hot or cold? -__________________________________________________________

Steam Traps

_____Service accessibility- can trap covers be removed

_____Required vertical inlet leg provided ahead of trap

Inlet leg specified in CD's:_____________  Inlet leg provided _____________

_____Trap check valves installed where rising after trap (drips)

_____No rise in condensate line after trap

(MANDATORY for traps serving any equipment controlled by modulating control valves: PROVIDE CORRECT INLET LEG HEIGHT UPSTREAM OF TRAP(S),  AND NO PIPE RISE DOWNSTREAM OF TRAP(S))

_____Drip before control valves

_____Trap iso. valves

_____Unions at traps

_____Dirt legs

Expansion Tank

Required Precharge (not "factory" charge):_________________

_____Verify precharge pressure (tank must be isolated from system and drained to set or verify pre-charge pressure.  Do not assume/use factory precharge)

_____Precharge pressure marked on tank?

_____Connected off side of main? (if off bottom, dirt leg and blowdown valve installed?)

_____Minimum 1" pipe size connection to main?

_____Auto air vent at top of 1" connection if connection rises above tank inlet

_____Tank connected as close as possible to pump suction

_____Anti siphon loop installed (12"-20" depth minimum)

_____Series B (Bladder Type) Tanks: 16" clear over bladder flange for bladder removal?

_____Data plate legible

Air Separator

_____Valved blow-down/drain installed

_____Air vent in top installed

_____Supported at nozzles

(Units greater than 8" pipe size must be supported by body, not by piping or nozzles))

_____Data plate legible

Air Vents General (all locations on system)

_____Installed at all system high points

_____Correct type (typically ball valves)

_____Correctly installed: (top of pipe)

_____Correct termination

Auto Air Vents (all locations on system)

_____Vent cap open only 1 full turn to prevent rapid air bleed?

_____ S igns of excess water discharge?

_____Piped to drain?

_____Isolation valve for vent

Drains (all locations on system)

_____Drains: at all low points

_____Correct type (typically ball valves)

_____Correctly installed: (bottom of pipe)

_____Correct termination (hose connector) :

Insulation

_____Complete

_____Correct label nomenclature

_____Correct arrow directions

Controls

_____Control air line for control valve(s) terminated at the valve and the DDC panel.

Contrcator controls complete:

______ DDC controls

______ Pneumatic Controls

UM DDC Shop Complete:

______ DDC Controls

General

_____Gages positioned to be readable

_____Gage scale ranges reasonable (spec./submittal)

_____Dirt/grime cleaned up

Pumps (use Pump Pre-start form)

Variable Frequency Drives (use VFD Pre-Start form)

List of other issues ___________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

___________________________________________________________________________________

Certification:  I certify the above checks have been made (signed/date)