PRE-START CHECKLIST- 3.43 HEAT RECOVERY SYSTEM

University of Michigan Plant Extension

Commissioning & Plan Review Department

Phone (734) 615-7168  Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer at least 7 days in advance of the actual equipment start-up. Note “NA” for not applicable or “NO” for problem or non-compliance. This document is to be used in conjunction with the manufacturer’s pre-start checklist.

Project Name: XXX					Project Number: XXXX-XX-XXX

Check     Item	Comments

##### AHU 1 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### AHU 2 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### AHU 3 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### AHU 4 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### AHU 5 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### AHU 6 Heat Recovery Coil

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ 3-way control valve installed at each coil bank_____________________________________________

___ Isolation valve & balance valve installed in 3-way by-pass____________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg after 3-way valve _____________________________________

___ Coil Fins Combed___________________________________________________________________

##### HRC-1E  Exhaust Heat Recovery Unit

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg ___________________________________________________

___ Coil Fins Combed___________________________________________________________________

___ Drain pan installed and piped per Cooling Coil Drain Pan Detail______________________________

___ Filters Installed _____________________________________________________________________

___ By-pass dampers (3) adjusted __________________________________________________________

##### HRC-3E  Exhaust Heat Recovery Unit

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg ___________________________________________________

___ Coil Fins Combed___________________________________________________________________

___ Drain pan installed and piped per Cooling Coil Drain Pan Detail______________________________

___ Filters Installed _____________________________________________________________________

___ By-pass dampers (3) adjusted __________________________________________________________

##### HRC-4E  Exhaust Heat Recovery Unit

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg ___________________________________________________

___ Coil Fins Combed___________________________________________________________________

___ Drain pan installed and piped per Cooling Coil Drain Pan Detail______________________________

___ Filters Installed _____________________________________________________________________

___ By-pass dampers (3) adjusted __________________________________________________________

##### HRC-5E  Exhaust Heat Recovery Unit

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg ___________________________________________________

___ Coil Fins Combed___________________________________________________________________

___ Drain pan installed and piped per Cooling Coil Drain Pan Detail______________________________

___ Filters Installed _____________________________________________________________________

___ By-pass dampers (3) adjusted __________________________________________________________

##### HRC-6E  Exhaust Heat Recovery Unit

___ Pressure gauges installed at each coil bank______________________________________________

___ Thermometers installed at each coil bank______________________________________________

___ Flow meter installed for coil bank ____________________________________________________

___ Air vent w/ball valve installed at each coil______________________________________________

___ Drain installed at each coil_____________________________________________________________

___ Test ports installed at each coil return______________________________________________

___ Throttling valve installed at each coil return______________________________________________

___ Isolation valve installed on return leg ___________________________________________________

___ Coil Fins Combed___________________________________________________________________

___ Drain pan installed and piped per Cooling Coil Drain Pan Detail______________________________

___ Filters Installed _____________________________________________________________________

___ By-pass dampers (3) adjusted __________________________________________________________

P-1   PUMPS

___ Nameplate Data Label secure, complete, legible and undamaged ______________________________

___ Electrical complete __________________________________________________________________

___ Fasteners tightened __________________________________________________________________

___ Equipment clean ____________________________________________________________________

___ Maintenance clearance is adequate ______________________________________________________

___ Manufacturer pre start checks complete __________________________________________________

___ Housekeeping pad proper height _______________________________________________________

___ Vibration isolators (aligned, weight even distributed, free floating) ____________________________

___ Pump base anchored and grouted _______________________________________________________

___ Pump and Motor complies with approved shop drawings ____________________________________

___ Piping complete ____________________________________________________________________

___ Pressure testing complete _____________________________________________________________

___ Removed Coupling Guard; checked coupling alignment, checked pump and motor anchor bolts______

___ Pump aligned and shimmed by: _______________ Alignment method__________________

___ Bearings greased with proper grease ____________________________________________________

___ Rotated pump by hand (no binding, grinding) _____________________________________________

___ Bumped motor. Checked and corrected rotation ___________________________________________

___ Coupling guard off and ready for inspection by UM Cx ______________________________________

___ Pipe hangers (no weight on pump) ______________________________________________________

___ System traced for proper installation. (correct flow) ________________________________________

P-2   PUMPS

___ Nameplate Data Label secure, complete, legible and undamaged ______________________________

___ Electrical complete __________________________________________________________________

___ Fasteners tightened __________________________________________________________________

___ Equipment clean ____________________________________________________________________

___ Maintenance clearance is adequate ______________________________________________________

___ Manufacturer pre start checks complete __________________________________________________

___ Housekeeping pad proper height _______________________________________________________

___ Vibration isolators (aligned, weight even distributed, free floating) ____________________________

___ Pump base anchored and grouted _______________________________________________________

___ Pump and Motor complies with approved shop drawings ____________________________________

___ Piping complete ____________________________________________________________________

___ Pressure testing complete _____________________________________________________________

___ Removed Coupling Guard; checked coupling alignment, checked pump and motor anchor bolts______

___ Pump aligned and shimmed by: _______________ Alignment method__________________

___ Bearings greased with proper grease ____________________________________________________

___ Rotated pump by hand (no binding, grinding) _____________________________________________

___ Bumped motor. Checked and corrected rotation ___________________________________________

___ Coupling guard off and ready for inspection by UM Cx ______________________________________

___ Pipe hangers (no weight on pump) ______________________________________________________

___ System traced for proper installation. (correct flow) ________________________________________

Ductwork:

___Ductwork Labeled with system name/ flow direction

___Correct type of duct hangers installed

___Correct installation of duct hangers

___No debris in ductwork

Piping System

___ Check piping and valves for leaks. Open and close valves to check for proper operation

___ Conduit/ Flex connections correctly installed

___ Flexible connections not torqued/misaligned

___ System Labeled with Tag Name

___ Misc. bolts/ fasteners tight

___ Vibration isolators (aligned, weight even distributed, free floating)

___Gages positioned to be readable

___Gage scale ranges reasonable (spec./submittal)

___ Relief Valve(s) pressure set at ____________.

# Flush, Clean, and Fill

___System water piping has been flushed and cleaned

___Strainers clean

___System properly vented

___System has been filled with glycol factory pre-mix with DI water.

# Expansion Tank

Required Pre-charge (not "factory" charge):_________________

___Verify pre-charge pressure (tank must be isolated from system and drained to set or verify pre-charge pressure.  Do not assume/use factory pre-charge)

___Pre-charge pressure marked on tank?

___Connected off side of main? (if off bottom, dirt leg and blow down valve installed?)

___ Pipe sized to match expansion tank connection size?

___Auto air vent at top of  connection

___Tank connected as close as possible to pump suction

___Series B (Bladder Type) Tanks: 16" clear over bladder flange for bladder removal?

___Data plate legible

# Air Separator

___Valved blow-down/drain installed

___Air vent in top installed on 1”  pipe

___Supported at nozzles

(Units greater than 8" pipe size must be supported by body, not by piping or nozzles)

___Data plate legible

# Glycol Feed System

___Electrical complete

___Fill pressure set at 45 psi

___DDC connected to low glycol reserve alarm.

___Glycol tank  filled with glycol solution.

___ Unit secured to floor

# Air Vents General (all locations on system)

___Installed at all system high points

___Correct type (typically ball valves)

___Correctly installed: (top of pipe)

___Correct termination (hose connection or piped to drain)

# Auto Air Vents (all locations on system)

___Vent cap open only 1 full turn to prevent rapid air bleed?

___ Signs of excess water discharge?

___Piped to drain?

___Isolation valve for vent installed

# Drains (all locations on system)

___Drains: at all low points

___Correct type (typically ball valves)

___Correctly installed: (bottom of pipe)

___Correct termination (hose connector)

# Insulation

___Complete

___Correct label nomenclature

___Correct arrow directions

# Controls

____Controls pre-start completely filled out.

Contractor controls complete:

___ DDC controls

___ Pneumatic Controls

UM DDC Shop Complete:

___ DDC Controls

System Functional Test:

___ Functional Test scheduled for: Day: ___________________ Time: ______________

___ Functional Test to be conducted by: __________________________

___ Completed Pre-start provided to UM commissioner 7 days in advance of scheduled Functional Test.

___ Notification provided to UM commissioner 7 days in advance of scheduled Functional Test.

Remarks:

______________________________________________________________________________

______________________________________________________________________________

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________