FUNCTIONAL TEST - HEATING HOT WATER SYSTEM

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Attendees:

1) _________________________________________ 2)____________________________________

3) _________________________________________ 4)____________________________________

5) _________________________________________ 6)____________________________________

7) _________________________________________ 8)____________________________________

Check     Item	Comments

Is system operating or is this initial start-up? __________________________________________________

Is the Pre-Start Checklist Complete? ________________________________________________________

Is all piping complete? ___________________________________________________________________

General:

___Gages positioned to be readable

___Gage scale ranges reasonable (spec./submittal)

# Heat Exchanger:

___No pipe weight, torque, or miss-alignment on flanges

___Space adequate for tube pull

___HX data plate readable and not concealed (by insulation, etc.)

___ Relief Valve(s) installed on water side

___ Relief Valve capacities ______________

___ Relief Valve Discharge to floor drain.

# Vacuum Breakers

___Installed on each HX

___ Adjusted for lowest vacuum setting

_____Lock nut tight.

# PRV/City Water Makeup

___Bypass closed

___PRV set?

Setting ______________ PSIG

___Gage Reading (downstream side of PRV)__________________ PSIG

System is hot or cold? -__________________________________________________________

# Steam Traps

___Service accessibility- can traps  be removed

___Required vertical inlet leg provided ahead of trap

Inlet leg specified in CD's:_____________  Inlet leg provided _____________

___No rise in condensate line after trap

___Drip before control valves

___Trap isolation valves

___Unions at traps

___Dirt legs

# Expansion Tank

Required Pre-charge (not "factory" charge):_________________

___Verify pre-charge pressure (tank must be isolated from system and drained to verify pre-charge pressure.  Do not use factory pre-charge)

___Pre-charge pressure marked on tank?

___Connected off side of main? (if off bottom, dirt leg and blow down valve installed?)

___Minimum 1" pipe size connection to main?

___Auto air vent at top of 1" connection if connection rises above tank inlet

___Tank connected as close as possible to pump suction

___Series B (Bladder Type) Tanks: 16" clear over bladder flange for bladder removal?

___Data plate legible

# Air Separator

___Valved blow-down/drain installed

___Air vent in top installed

___Data plate legible

# Air Vents General (all locations on system)

___Installed at all system high points

___Correct type (typically ball valves with automatic air vent)

___Correctly installed: (top of pipe)

___Correct termination

# Auto Air Vents (all locations on system)

___Vent cap open only 1 full turn to prevent rapid air bleed?

___ Signs of excess water discharge?

___Piped to drain?

___Isolation valve for vent

# Drains (all locations on system)

___Drains: at all low points

___Correct type (typically ball valves)

___Correctly installed: (bottom of pipe)

___Correct termination (hose connector)

# Insulation and Label

___Complete

___Correct label nomenclature

___Correct arrow directions

# Controls

Contractor controls complete:

___ DDC controls

___ Pneumatic Controls

UM DDC Shop Complete:

___ DDC Controls

# Pumps (Use Pump Functional Test form)

# Variable Frequency Drives (Use VFD Functional Test form)

Remarks:

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________