PRE-START CHECKLIST- HEATING HOT WATER SYSTEM

University of Michigan Plant Extension

Commissioning & Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer at least 7 days in advance of the actual equipment start-up. Note “NA” for not applicable or “NO” for problem or non-compliance. This document is to be used in conjunction with the manufacturer’s pre-start checklist.

Project Name: 	XXX				Project Number: XXXX-XX-XXX

Provide identifying information for the following equipment, as applicable: heat exchangers, expansion tanks, air separators,

Tag No. 			Model No. 				Serial No.

Check     Item	Comments

General:

___ Nameplate Data Labels secure, complete, legible and undamaged ______________________________

___ Electrical complete __________________________________________________________________

___ Controls complete ___________________________________________________________________

___ Fasteners tightened __________________________________________________________________

___ Equipment clean ____________________________________________________________________

___ Maintenance clearance is adequate _____________________________________________________

___ Manufacturer pre-start checks complete__________________________________________________

___ Check piping and valves for leaks. Open and close valves to check for proper operation

___ Data label info matches approved submittal

___ Conduit/ Flex connections correctly installed

___ Flexible connection not torqued/misaligned

___ System Labeled with Tag Name

___ Misc. bolts/ fasteners tight

___ Vibration isolators (aligned, weight even distributed, free floating)

___Gages positioned to be readable

___Gage scale ranges reasonable (spec./submittal)

# System Piped Per Design Drawings and Code

___ Make-up water

___ Heating hot water piping

___ Steam piping

___ Equipment is installed in strict compliance with design documents/specification and per manufacturers installation instructions.

# Flush, Clean, and Fill

___System water piping has been flushed and cleaned

___System steam and condensate piping has been flushed and cleaned

___Strainers clean, steam side

___Strainers clean, HHW Side

___System piping has been filled and properly vented

# Heat Exchanger:

___No pipe weight, torque, or miss-alignment on flanges

___Adequate support for HX

___If bolted to floor, feet or bracket mounting bolts loose to allow expansion

___Room for tube pull

___Data plate readable and not concealed (by insulation, etc.)

___ Relief Valve(s) installed on water side

___ Relief Valve capacities checked against HX nameplate.

___ Relief Valve Discharge piped per Code

# Vacuum Breakers

___Installed on each HX

___Bottom adjustment nut adjusted high on threads so vent operates under low vacuum condition?

(If nut is low on threads vent will not open until high vacuum occurs, effecting HX modulation)

_____Top jam nut tight against bottom adjustment nut?

# PRV/City Water Makeup

___Bypass closed

___PRV set?

Setting ______________ PSIG

___Gage Reading (downstream side of PRV)__________________ PSIG

System is hot or cold? -__________________________________________________________

# Steam Traps

___Service accessibility- can trap covers be removed

___Required vertical inlet leg provided ahead of trap

Inlet leg specified in CD's:_____________  Inlet leg provided _____________

___Trap check valves installed where rising after trap (drips)

___No rise in condensate line after trap

(MANDATORY for traps serving any equipment controlled by modulating control valves: PROVIDE CORRECT INLET LEG HEIGHT UPSTREAM OF TRAP(S),  AND NO PIPE RISE DOWNSTREAM OF TRAP(S))

___Drip before control valves

___Trap isolation valves

___Unions at traps

___Dirt legs

# Expansion Tank

Required Pre-charge (not "factory" charge):_________________

___Verify pre-charge pressure (tank must be isolated from system and drained to set or verify pre-charge pressure.  Do not assume/use factory pre-charge)

___Pre-charge pressure marked on tank?

___Connected off side of main? (if off bottom, dirt leg and blow down valve installed?)

___Minimum 1" pipe size connection to main?

___Auto air vent at top of 1" connection if connection rises above tank inlet

___Tank connected as close as possible to pump suction

___Series B (Bladder Type) Tanks: 16" clear over bladder flange for bladder removal?

___Data plate legible

# Air Separator

___Valved blow-down/drain installed

___Air vent in top installed

___Supported at nozzles

(Units greater than 8" pipe size must be supported by body, not by piping or nozzles))

___Data plate legible

# Air Vents General (all locations on system)

___Installed at all system high points

___Correct type (typically ball valves)

___Correctly installed: (top of pipe)

___Correct termination

# Auto Air Vents (all locations on system)

___Vent cap open only 1 full turn to prevent rapid air bleed?

___ Signs of excess water discharge?

___Piped to drain?

___Isolation valve for vent

# Drains (all locations on system)

___Drains: at all low points

___Correct type (typically ball valves)

___Correctly installed: (bottom of pipe)

___Correct termination (hose connector) :

# Insulation

___Complete

___Correct label nomenclature

___Correct arrow directions

# Controls

___Control airline for control valve(s) terminated at the valve and the DDC panel.

Contractor controls complete:

___ DDC controls

___ Pneumatic Controls

UM DDC Shop Complete:

___ DDC Controls

# Pumps (Use Pump Pre-Start form)

# Variable Frequency Drives (Use VFD Pre-Start form)

System Start-Up:

# At least two weeks prior to start-up

___ Equipment installation manuals have been submitted to UM Cx

___ Controls contractor generated "Commissioning Manual" (functional test procedure) has been submitted to the UM Cx

# At least one week prior to start-up

___ Equipment/System Start-up Notification Form has been faxed to the UM Cx agent

___ Start-up scheduled for: ____________________, to be conducted by: __________________________

___ Start-up notification faxed to UM commissioner 7 days in advance of scheduled start-up.

Remarks:

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________