PRE-START CHECKLIST- COMPRESSED AIR DRYER

University of Michigan Plant Extension

Commissioning & Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer at least 7 days in advance of the actual equipment start-up. Note “NA” for not applicable or “NO” for problem or non-compliance. This document is to be used in conjunction with the manufacturer’s pre-start checklist.

Project Name: XXX		 			Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Check     Item	Comments

Air Dryer

___ Nameplate Data Label secure, complete, legible and undamaged ______________________________

___ Electrical complete __________________________________________________________________

___ Equipment Grounded ________________________________________________________________

___ Maintenance clearance is adequate______________________________________________________

___ Unit data label info matches approved submittal

___ Automatic Purge Saving System provided

___ Unit Labeled with Tag Name

___ Voltage selection switch set/ verified

___ Pressure selection dip switch set/ verified

___ Mode / Cycle selection dip switches set/ verified (10 minute cycle)

___ Purge rate valve adjusted

___ Prefilter with automatic demand drain valve installed

___ Afterfilter installed

___ Automatic drain valves piped to floor drain _______________________________________________

___ Shutoff valves installed _______________________________________________________________

___ Manual by-pass installed ______________________________________________________________

___ Air Load is available _________________________________________________________________

System

___ Pressure Regulating Valve Installed

___ Safety Relief Valve Installed

___ Start-up scheduled for: ____________________, to be conducted by: __________________________

___ Start-up notification faxed to UM commissioner 7 days in advance of scheduled start-up.

Remarks:

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________