PRE-START CHECKLIST- EXHAUST FAN

University of Michigan Plant Extension

Commissioning & Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer at least 7 days in advance of the actual equipment start-up. Note “NA” for not applicable or “NO” for problem or non-compliance. This document is to be used in conjunction with the manufacturer’s pre-start checklist.

Project Name: XXX					Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Check     Item							Comments

General:

___ Nameplate Data Label secure, complete, legible and undamaged ______________________________

___ Electrical complete __________________________________________________________________

___ Controls complete ___________________________________________________________________

___ Fasteners tightened __________________________________________________________________

___ Equipment clean ____________________________________________________________________

___ Maintenance clearance is adequate _____________________________________________________

___ Manufacturer pre start checks complete _________________________________________________

Fan:

___ Has fan been aligned after installation?	        	By whom?

___ Fan shaft parallel to motor shaft

___ Pulleys at right angles to shafts

___ Preliminary belt tension checked and corrected

Note- unless otherwise specified by the fan mfg. , belts are considered correctly adjusted if center deflection at midpoint = 1/64" per inch of belt span.  Belt span = center to center pulley distance.  Example: 15" between pulley centers, correct deflection 15/64" or approx. ¼" with moderate pressure applied at midpoint between pulleys

___ Fan off/drive disconnected/rotate by hand/no drag

___ No trash in scroll

___ Fan data label info matches approved submittal

___ Fan Labeled with Tag Name (15075)

___ Bearings Greased, extended lube lines filled

___ Misc. bolts/ fasteners tight

Ductwork:

___Ductwork Labeled with system name/ flow direction (15075)

___Correct type of hangers installed

___Correct installation of hangers

___No debris in ductwork

___Instrument test holes provided (15820)

Electrical:

___Electrical connectors and terminals tightened

___Proper thermal-overload at starters and disconnects

___Motor rotation correct

___Power connection to fan is in conduit with flex connection to motor

Note – Belt guard to be off for Cx inspection at Functional Test.

Fan System Start-Up:

___ Start-up scheduled for: ____________________, to be conducted by: __________________________

___ Start-up notification faxed to UM commissioner 7 days in advance of scheduled start-up.

Remarks:

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________