FUNCTIONAL TEST – RO/DI SYSTEM

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Tag No.			Model No.			Serial No.

Attendees:

1) _________________________________________ 2)____________________________________

3) _________________________________________ 4)____________________________________

5) _________________________________________ 6)____________________________________

7) _________________________________________ 8)____________________________________

9) _________________________________________ 10)___________________________________

Check     Item							Comments

___Is system operating or is this initial start-up? _______________________________________________

___Is the Pre-Start Checklist Complete? _____________________________________________________

Maximum amp draw (A/B/C): _____ / _____ / _____

Measured amp draw (A/B/C): _____ / _____ / _____

Design voltage (AB/BC/AC): _____ / _____ / ____

Measured voltage (AB/BC/AC): _____ / _____ / _____

Verify Rotations

Booster Pump		Repressure Pump			RO Pump

Verify HOA "hand" position, each pump

Booster Pump		Repressure Pump			RO Pump

No excess vibration when pumps are running

Demonstrate booster pump cycling

Demonstrate RO turns on under low tank conditions (TLS1)

Demonstrate repressure pump and UV cycle off under low tank conditions (TLS2)

Demonstrate softener resin bottle changeover based on water meter

Demonstrate RO controller alarms

Low inlet water pressure		Low outlet water pressure

Demonstrate RO shutdown on low inlet pressure condition

Verify RO tank PRV setting and demonstrate operation of PRV

RO water is being delivered to distribution piping and equipment

Required RO setpoint:

Actual RO setpoint:

Functional Tests Specific to This Unit (list)

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Remarks:

Witnessed By:						Date:

U of M Commissioner