Pre-Start Check List

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone: (734) 615-7168   Fax: 936-3334

This document shall be filled out by the contractor and provided to the UM Commissioning Engineer in advance of actual equipment start-up.  Note "NA" for not applicable, "NO" for problem or non-compliance.  This document is to be used in conjunction with the manufacturer's pre-start checklist.

Editors note: Prestart not complete, needs to be done.  Function test form OK but not 100%.

Project Name:

Project Number:

Completed by/representing (print):

# RO Water Systems

Tag No. 			Model No. 				Serial No.

Check		Item					Comments

Comments: ___________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Certification:  I certify the above checks, and any specific checks or procedures required by the manufacturer's installation instructions, have been made (signed/date).

Functional Test

University of Michigan

Facilities Evaluation and Commissioning Dept.

Project Name:

Project Number:

Completed by/representing (print):

# RO Water Systems

General

Nameplate data plates legible.  Nameplate securely attached.

Model numbers match approved submittal.

Piping arrangement matches' construction documents (including material: sch. 80 PVC)

Piping adequately supported

Piping properly labeled

Sufficient maintenance clearance exists at all components

Tanks adequately supported (base)

All drains are PVC, run to floor drains, and air gapped

BFP installed.  Minimum 12" air gap from discharge port to floor

Throttling globe valve installed on each pump discharge

Piping was pressure tested.  No obvious leaks currently exist

All fasteners tight

All wiring between components is in seal tight

All wiring between components is labeled

Skid is bolted to floor

Verify equipped w/5 micron 20" long prefilter

Sample points installed at: CW inlet, discharge of softener, carbon filter, RO unit, and UV light

All mfg. prestart checks complete

Installation is strictly per mfg. installation instructions

Functional Test

Verify Rotations

Booster Pump		Repressure Pump			RO Pump

Verify HOA "hand" position, each pump

Booster Pump		Repressure Pump			RO Pump

No excess vibration when pumps are running

Demonstrate booster pump cycling

Demonstrate RO turns on under low tank conditions (TLS1)

Demonstrate repressure pump and UV cycle off under low tank conditions (TLS2)

Demonstrate softener resin bottle changeover based on water meter

Demonstrate RO controller alarms

Low inlet water pressure		Low outlet water pressure

Demonstrate RO shutdown on low inlet pressure condition

Verify RO tank PRV setting and demonstrate operation of PRV

RO water is being delivered to distribution piping and equipment

Required RO setpoint:

Actual RO setpoint:

Functional Tests Specific to This Unit (list)

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Comments: ___________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

Commissioning and Certification: (Names, firms, and date):

Certification:  I certify the above checks and tests were successful, the system is installed per the mfg.'s instructions, and any specific checks or procedures required by the manufacturer's installation instructions have been made.