FUNCTIONAL TEST – Server Cooling System

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Attendees:

1) _________________________________________ 2)____________________________________

3) _________________________________________ 4)____________________________________

5) _________________________________________ 6)____________________________________

7) _________________________________________ 8)____________________________________

Is system operating or is this initial start-up? __________________________________________________

Is the Pre-Start Checklist Complete? ________________________________________________________

Is all piping complete? ___________________________________________________________________

Proper Number of Floor Grilles installed_____________________________________________________

Floor Plenum sealed and floor panels fit._____________________________________________________

Pump CHWP-7 & 8

Pump mfg. start-up report obtained: _______________________________________________________

Pump data plate legible: ________________________________________________________________

Pump rotation verified: _________________________________________________________________

Flexible connections not torqued/mis-aligned: ________________________________________________

Flexible connection restraining bolts not over tighten: __________________________________________

Inertia base clears floor and is free to move? __________________________________________________

Dead head pump, run at full speed, record pressure differential: ___________________________________

Pump dead head pressure matches curve dead head?: ___________________________________________

Unusual vibration? ______________________________________________________________________

Unusual noise? _________________________________________________________________________

DDC monitors correct pump status_________________________________________________________

DDC will alternate Pumps________________________________________________________________

Liebert Units 1,  2,  3

Units Operated 24 hours without Error Messages ______________________________________________

Unit in good condition ___________________________________________________________________

Unit hot gas by-pass reheat mode operates ___________________________________________________

Unit Electric reheat mode operates _________________________________________________________

Unit Cools_______ _____________________________________________________________________

Unusual vibration? ______________________________________________________________________

Unusual noise? _________________________________________________________________________

DDC Monitors general trouble alarm from each Liebert_________________________________________

Remarks:

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________