FUNCTIONAL TEST – SPECIALTY GAS

University of Michigan Plant Extension

Commissioning and Plan Review Department

Phone (734) 615-7168 Fax (734) 936-3334

This is not a punch list.  The engineer of record, not the commissioning team, performs Punch listing.

Project Name: XXX					Project Number: XXXX-XX-XXX

Room  No.:___________________

____GCC-1: One cylinder cabinet with (1) one valve gas panel

____GCC-2: Two cylinder cabinet with (2) one valve gas panels

____GCC-2S: Two cylinder cabinet with (1) series switchover system

____GCC-3: Three cylinder cabinet with (3) one valve gas panels

Gas Cabinet:

___ Fasteners tightened __________________________________________________________________

___ Equipment clean ____________________________________________________________________

___ Equipment undamaged _______________________________________________________________

___ Integral fire protection sprinkler connected

___ Door closer operates smoothly

___ Door Seals

___ Latch Operates

#1 - One Valve Panel:

___ Process valve operates _______________________________________________________________

___ Pigtail provided ____________________________________________________________________

___ Cylinder Pressure Gauge Operates ______________________________________________________

___ Delivery Pressure Gauge Operates

___ Line Regulator controls from 0-100 psi

#2 - One Valve Panel:

___ Process valve operates _______________________________________________________________

___ Pigtail provided ____________________________________________________________________

___ Cylinder Pressure Gauge Operates ______________________________________________________

___ Delivery Pressure Gauge Operates

___ Line Regulator controls from 0-100 psi

#3 - One Valve Panel:

___ Process valve operates _______________________________________________________________

___ Pigtail provided ____________________________________________________________________

___ Cylinder Pressure Gauge Operates ______________________________________________________

___ Delivery Pressure Gauge Operates

___ Line Regulator controls from 0-100 psi

Switchover System:

___ Pigtails provided ____________________________________________________________________

___ Cylinder Pressure Gauges (2) Operate____________________________________________________

___ Delivery Pressure Gauge Operates

___ Line Regulator controls from 0-100 psi

___ Swtchover Regulator opeates

## Completed by (print): _______________________Company: __________________________

Signed: _______________________________________ Date: _________________________________