Pre-Start-Functional Test

University of Michigan

Facilities Evaluation and Commissioning Dept.

Phone: (734) 615-7168   Fax: 936-3334

Project Name:

Project Number:

Completed by/representing (print):

# Steam Humidifiers

Tag No. 			Model No. 				Serial No.

Dispersion Tubes

Number of tubes installed matches the submittal

Tubes pitched back toward tube header (typically 2"/ft)

Steam pipe from HX to dispersion tube header is pitched down back toward HX (typically 2"/ft)

Dispersion tube orifices are pointing up (in duct) (access door installed at wands)

Dispersion tubes supported on outboard end of duct

No lifting of condensate lines after steam traps

Controller high limit is 10' from wands

No directional changes, duct obstructions, control transmitters, etc. prior to high limit

Proper water trap depth on dispersion tube header

Water trap on dispersion tube header is primed

Proper Duct downstream of the humidifier

General

All mfg. prestart checks complete

Installation is strictly per mfg. installation instructions

Steam evaporates in duct before impinging on high limit

Controller high limit functions

All safeties function

Note: It is usually impractical to functionally test humidifiers at their maximum capacity.  Therefore this report only verifies that there were no apparent functional problems at the time of the test.  Inadequate absorption distances in particular may not become apparent until weather conditions exist that require the humidifier to operate at maximum capacity.

Comments: ___________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________

_____________________________________________________________________________________