**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

**ARCHITECTURE, ENGINEERING AND CONSTRUCTION**



ARCHITECTURE & ENGINEERING

326 East Hoover, Mail Stop B

Ann Arbor, MI 48109-1002

Phone: 734-764-3414

Fax: 734-936-3334

BuildingName  
The Description of the Project  
P00000000 0000

DOCUMENTS

SPECIFICATION DIVISION 23

NUMBER SECTION DESCRIPTION

DIVISION 23 HEATING, VENTILATING AND AIR CONDITIONING (HVAC)

SECTION 232516 – CHEMICAL WATER TREATMENT - OPEN LOOP SYSTEMS

END OF CONTENTS TABLE

1. DIVISION 23 HEATING, VENTILATING AND AIR CONDITIONING (HVAC)
   1. SECTION 232516 – CHEMICAL WATER TREATMENT - OPEN LOOP SYSTEMS

New March 2013.

This SPECIFICATION is designed for chilled water cooling tower CONDENSER water systems and may need revision if used for other open loop systems, such as evaporative coolers and air washers.

the chilled water system at university hospital is a hybrid closed/open loop system; this specification must be specially modified when used for work on that system. contact the u-m design manager for direction.

Added spec for injection quill. D. Karle for Hydronics MTT 6/17/2013.

Enhanced the description of bromine tablets per recommendation from M. Willet and M. Mau. D. Karle 9-5-2013.

***Jan. 2017: Added U.S. Water as approved CSP per Stm/Hydronics MTT. d. karle***

Sept. 2017: Removed GE water as approved csp per hydronics and steam MTT due to poor service. d. karle

June 2018: Added Novatech and ADVANTAGE Controls as APPROVED mfr.s for coupon racks, deleted Vector Industries (Does not make racks), per request of Facilities Maintenance/N. Vanderkolk. Improved coupon rack description similar to CLOSED loop spec. d. karle.

Feb. 2019: Revised Crown Solutions to Veolia Water, new corporate name. d. karle

* + 1. GENERAL
       1. related doCUMENTS

INCLUDE PARAGRAPH 1.1.A and b IN EVERY SPECIFICATION SECTION. EDIT related sections 1.1.B to make it project specific.

* + - * 1. Drawings and general provisions of the Contract, Standard General and Supplementary General Conditions, Division 1 Specification Sections, and other applicable Specification Sections, in particular the Related Sections listed below, apply to this Section.

IN 1 and 2 BELOW, SELECT PROPER SPEC SECTION NUMBER by project. delete Sustainable design / leed if not applicable to project. Delete Commissioning if not applicable to project.

* + - * 1. Related Sections:

Section 019110/019100 - Commissioning

Section 220500 - Common Work Results for Mechanical

Section 221113 - Piping Materials and Methods

Section 220523 - Valves

Section 220553 - Mechanical Identification

Section 230900 – Mechanical Systems Controls

Section 26 – Electrical

* + - 1. summary
         1. Products for chemical water treatment systems specified in this section include the following:

Chemical Inhibitors and Biocides for Water

Motor Operated Ball Valves

Chemical Feed Pumps

Bromine Feeder Tank

Chemical Treatment Controller with Conductivity Probe and flow switch.

Corrosion Coupon Rack

Solid Corrosion Inhibitor Dissolver

Clear Plastic Strainers

Flow Indicators

Ball Valves

Injection Quill Assembly

Chemical Solution Tubing

* + - * 1. Provide a Chemical Services Provider (CSP) to perform the services described below.
        2. Provide water treatment products and services including:

Chemicals for cleaning, passivation, and treatment of each system.

On-going treatment, chemicals, testing, certification, and reports to demonstrate effective water treatment is maintained at all times.

Start-up and operation of chemical treatment equipment.

* + - * 1. Provide a complete chemical water treatment program during construction for all new and reused piping networks. This program shall begin from the point each system is filled during construction and extend until Substantial Completion or final Owner acceptance of each system, whichever occurs later. The programshall include water analysis, chemicals, testing, equipment, consulting and service for the following systems:

Revise below, the systems covered by this spec for your particular PROJECT.

Chilled Water Condenser Water System

* + - * 1. Attend project meetings as required to plan, schedule and coordinate above activities with other project contractors and the Owner.
        2. Provide recommended testing procedures and chemical treatment schedule for Owner's personnel. This information shall be submitted to the owner in a Program Administration Manual.
      1. SUBMITTALS
         1. Product Data: Include rated capacities; water-pressure drops; shipping, installed, and operating weights; and complete data on furnished products listed below:

Product specifications and MSDS’s for each chemical used

Cleaning Procedures

Passivation Procedures

Chemical Treatment Procedures

Motor Operated Ball Valves

Chemical Feed Pumps

Bromine Feeder Tank and Piping Kit

Chemical Treatment Controller with Conductivity Probe

Corrosion Coupon Rack

Solid Corrosion Inhibitor Dissolver

Clear Plastic Strainers

Flow Indicators

Ball Valves

Injection Quill

Chemical Solution Tubing

PVC back-board

* + - * 1. Schematic diagram of the water treatment system showing the arrangement of all components and piping connections.
        2. Project specific wiring diagram reflecting wiring between all devices and connections to Owner’s monitoring system.
        3. Details regarding the construction, support, and arrangement of devices on the PVC back-board.
        4. Submit resume of water treatment personnel and name of Chemical Services Provider.

Provide a current copy of CSPs State of Michigan Commercial Pesticide Applicators Category 5B certification.

* + - * 1. Service Reports as indicated under Part 2 below.
        2. Sequence of Operation: Provide a written sequence of operation detailing the operation of the chemical treatment system.
        3. Program Administration Manual.
        4. Passivation Confirmation Report(provide when passivation is specified): Verify passivation of galvanized-steel surfaces, and confirm this observation in a written report to the Architect and Construction Manager.
        5. Shop Drawings to include detailed equipment assemblies indicating dimensions, weights, loads, required clearances, method of field assembly, components, and the location and size of each field connection as necessary to assist the mechanical contractor with proper system installations.
      1. QUALITY ASSURANCE
         1. Manufacturers and Products: The manufacturer listed as the “Basis of Design” establishes the standard of quality that shall be provided for the Work. Subject to compliance with all requirements indicated and the features provided by the Basis of Design, provide specified products from the manufacturers named in Part 2.
         2. Products in this section shall be built, tested, and installed in compliance with the specified quality assurance standards; latest editions, unless noted otherwise.

American Society for Testing and Materials (ASTM)

D859 – Test Method for Silica in Water

D1067 – Test Methods for Acidity/Alkalinity in Water

D1068 – Test Methods for Iron in Water

D1126 – Test Method for Hardness in Water

D4012 - Test Method for Adenosine Triphosphate (ATP) Content of Microorganisms in Water

D5465 - Practice for Determining Microbial Colony Counts from Waters Analyzed by Plating Methods

NFPA 70 National Electric Code

* + - * 1. CSP shall be currently certified by the State of Michigan for Commercial Pesticide Application Category 5B.
        2. Chemicals shall comply with all Federal, State and Local/Municipal requirements as defined by the governing agencies.
        3. Conform to all applicable Codes, Regulations, and Municipal requirements for the use and disposal of chemicals (including cleaning compounds) and waste to public sewer systems.

Wastewater shall be discharged to the sanitary sewer only if it has a pH between 5.0 and 10.0 and meets the requirements of the City of Ann Arbor Sewer Use Ordinance. For wastewater not meeting such criteria, contact U-M Occupational Safety and Environmental Health (OSEH) Hazmat at 734-763-4568 for proper disposal instructions.

City of Ann Arbor Sewer Use Limitations can be found at the following Ann Arbor City website:<http://www.municode.com/resources/gateway.asp?pid=11782&sid=22> or by contacting U-M OSEH Environmental Protection & Permitting Program (EP3) at 734-936-1920.

Contact U-M OSEH HazMat at 734-763-4568 for special disposal requirements and proper disposal instructions.

Wastewater containing any chemical or sediment is prohibited from discharge to the storm water system. No chemical shall contain Chromates or Inorganic Phosphates.

* + - 1. DELIVERY, STORAGE, AND HANDLING
         1. Package for delivery to best protect finished surfaces while using the least amount of single-use packaging as possible. Deliver equipment and components adequately packaged for lifting, skidding, or rolling into final position, according to manufacturer's instructions. If possible, package and ship products using reusable blankets and fabrics, or reusable cardboard and crate systems.
         2. Store materials and equipment raised off the floor on pallets and protected with coverings to prevent damage due to weather and construction activities. Store in areas that prevent damage due to freezing and extreme temperatures or sunlight. Arrange coverings to provide air circulation to avoid damage from condensation or chemical build-up. Protect from damage, dirt and debris at all times.
         3. Store chemicals in curb protected area. Such secondary containment areas must have the capacity to hold the volume of the largest container or 10% of the combined containers, whichever larger. If room has no floor drains, then the room itself may be considered sufficient secondary containment. If the room is considered the secondary containment ensure there is a lip at the door so no liquids can exit the room in the event of a leak. Verify field conditions before storing any chemicals

Provide temporary containment areas when permanent containment areas do not exist. Remove temporary containment at the end of construction.

* + - 1. WARRANTY
         1. Provide a complete warranty for parts and labor for a minimum of one year from the date of Substantial Completion. This warranty does not include ongoing chemical treatment or monitoring.
      2. ACCEPTABLE CHEMICAL SERVICE PROVIDERS (CSP)
         1. Approved CSPs

Chemtreat

Veolia Water

Kroff

Mitco

Nalco

Rochester Midland

U.S. Water Services

* + 1. products
       1. GENERAL
          1. CSP Services:

The CSP shall provide all cleaning and treatment chemicals, basic services (including set-up and programming of all water treatment control devices), testing, equipment and materials necessary for a complete water treatment program.

The CSP shall perform an analysis of the supply water to determine the type and quantities of chemical treatment needed to maintain the required water quality to prevent corrosion, scaling, and biological growth. The CSP will at minimum provide weekly site visits to verify proper water treatment after any system or part of a system is treated. Weekly visits shall be conducted to assure performance requirements are being met, analyze water samples, inspect equipment, and adjust feed rates as required to maintain proper water treatment, and continue until final written Owner acceptance of the respective system.

At each site visit CSP shall analyze each system for corrosion inhibitors, pH, total iron, total copper, bacteria levels (provide analytical laboratory analysis monthly) and conductivity; inspect loss from corrosion coupons (provide analytical laboratory analysis monthly), record make-up meter readings, and perform any other tests necessary to validate that corrosion, scale, and organic growth is being prevented.

Reports:

Submit a written startup test report for each system placed into service.

A service report shall be prepared on site by the CSP, submitted at the time of each service visit (with copies immediately provided to the Owner and Commissioner), which shall include all required test results and recommendations.

Additionally, provide final reports for approval to the Owner and Commissioner regarding each site service visit, certified by an Officer of the CSP, within one week of any water treatment activity. Such reports shall include the results of any field or lab tests. Reports shall clearly state if the required water quality and maximum corrosion rates are being achieved.

At a minimum, each report shall include the following information (levels shall be reported in ppm unless noted otherwise):

System Treated

Date

Conductivity (microsiemens)

pH

Total Iron

Total Copper

Coupon Corrosion Rates (monthly analytical laboratory analysis)

Make-up Water Quantity Since Last Visit

Corrosion Inhibitor Level

Silica Level

Biocide Level

"P" Alkalinity

Free "OH" Alkalinity

Chemical Oxygen Demand

Total Suspended Solids (TSS)

Ammonia

Calcium Carbonate Hardness

Calcium Carbonate Alkalinity

Microbiological in organisms/mL (monthly analytical laboratory analysis)

Total Aerobic Plate Count

Total Anaerobic Plate Count

Nitrate Reducers

Sulfate Reducers

Iron Bacteria

Conduct final on-site system turn over meeting with Owner and Commissioner. Present final validation report demonstrating that performance requirements have been achieved and that each system is currently properly treated.

When required by Part 3, train Owner's maintenance personnel in water treatment procedures.

Program Administration Manual:

The CSP shall provide the Owner with two (2) Program Administration Manuals including sections covering program control, testing requirements, in plant logs, safety data and system information. Each section shall include the following:

Program Control: Include a complete program outline with chemical descriptions, control ranges, and required action for “out of range” situations. Also include complete ordering instructions with applicable account numbers and phone numbers.

Testing Requirements: This section will include basic testing practices as well as detailed test instructions for each test to be performed.

Sequence of operation detailing the operation of the chemical treatment system.

In-Plant Logs: Include detailed testing log sheets for each system to be tested including room to record one (1) month’s data on one (1) sheet and a section to log chemical inventory.

Safety Data: Include the CSP’s 24-hour toll free safety hotline number as well as MSDS sheets for each chemical used.

System Information: Include any equipment manuals and related information.

* + - 1. TREATMENT PROGRAM – FLUSHING AND CLEANING
         1. Cleaning chemicals shall be non-phosphate and non-acidic.
         2. Flush and clean all new and reused piping.
         3. Provide a flush/clean plan for approval. Provide and later remove all temporary bypasses, drains, vents, etc. required to flush and clean the system. Temporary components for flushing and cleaning are not indicated on the drawings.
         4. Flush and clean systems per the general procedures specified in Related Sections; clean systems per the approved cleaning procedures submitted under this specification section. Provide and install all required cleaning chemicals.
         5. Verify that adequate cleaning chemical was added and that cleaning was effective. Test that cleaning chemicals were properly rinsed from the system. Provide a report certifying that cleaning and rinsing, was properly executed.
         6. Provide chemical treatment immediately after each system has been cleaned and flushed. Systems shall not stand filled with fluids for periods longer than 48 hours without beginning flushing and cleaning of the system, which shall then be immediately followed by the chemical treatment procedures.
      2. CHEMICAL TREATMENT - general
         1. Provide passivation and chemical treatment per the submitted and reviewed chemical treatment procedures and Program Administration Manual and to maintain the Performance Requirements.
         2. Chemically treat new and reused piping networks using chemicals and treatment procedures compatible with the system being cleaned and the chemical treatment chemicals in existing piping systems being connected to. Test existing piping systems or otherwise determine chemical treatment in existing piping and validate compatibility.

The below PARAGRAPH in hidden text is for EQUIPMENT with substantial quantities of wet galvanized metal surfaces; unhide when appropriate. normal u-m practice is to require STAINLESS steel hot and cold water basins on COOLING towers in which case passivation is not considered necessary for the small amount of remaining galvanized components.

* + - * 1. Passivate cooling towers, evaporative coolers, and similar equipment with galvanized-steel components in strict compliance with manufacturers recommendations. Maintain the pH of the circulating water between 7.0 and 8.0 for a minimum of 8 weeks after start-up until zinc surfaces turn a dull gray color; maintain manufacturer’s recommended hardness and alkalinity levels during the passivation interval. If white deposits form on galvanized surfaces after pH is returned to normal service levels, repeat the passivation process until galvanized surfaces are properly passivated/no white deposits form.

When CONNECTing into existing active systems, develop requirements and a coordination plan in CONSULTATION with u-m plant and revise the below sample paragraph accordingly.

* + - * 1. When connecting into active existing systems, treat piping networks installed or reused by the project and verify by lab analysis that the treatment levels per the treatment plan have been attained prior to connecting into the existing active system. Submit validating report for approval.

Do not connect into existing active system until report is approved by Owner.

Provide temporary valves, piping, and accessories as required to treat the project’s piping prior to connection to the active system.

* + - * 1. Provide chemical treatment program at system startup or immediately upon operation of a system for temporary cooling, whichever comes first.
        2. Provide chemical treatment immediately after the system has been cleaned and flushed. Immediately thereafter, begin the approved water treatment maintenance program to passivate and prevent corrosion, scale, and organic growth and to maintain treatment chemical levels.
        3. Chemical inhibitors for open loop chemical systems shall be polymer based without molybdenum as a corrosion inhibitor and contain azole in an amount appropriate for the percentage of internal copper surface area of the system piping. Provide products with PTSA (p-Toluenesulfonic acid) florescent tracer dyes. Molybdenum shall not be used as a tracer.
        4. Use 1" halogenated isocyanurate bromine tablets for biological control.
        5. No chemicals shall contain chromates or inorganic phosphates.
        6. Adjust chemical concentrations as required to achieve the required performance.
      1. PERFORMANCE REQUIREMENTS
         1. The water treatment programs proposed by the CSP shall maintain corrosion rates below 0.5 mils per year for mild steel and 0.1 mils per year for copper. These rates shall be verified with corrosion coupons provided by the CSP. Coupons shall be analyzed in the CSP’s analytical laboratory monthly, or more often if required, to assure these levels are not exceeded.
         2. Microbiological growth levels shall be maintained below 10,000 cfu’s aerobic bacteria and 10 cfu’s anaerobic bacteria. The CSP shall perform detailed microbiological culturing at the CSP’s company’s analytical laboratory monthly, or more often if required, to assure these levels are not exceeded
         3. The Langelier Stability Index shall be maintained to not exceed 2.50.
      2. EQUIPMENT - GENERAL
         1. Provide all components required for a fully operational water treatment system. Provide components that are not adversely affected by the treatment chemicals employed, and that are rated for the maximum pressures and temperatures that may be encountered by the treatment system.

Designer must include U-M Detail 15710002 - Condenser Water Treatment Equipment Diagram on the design drawings.

* + - * 1. Refer to the condenser water treatment equipment detail for additional equipment requirements.
      1. Motor Operated Ball Valve:
         1. Acceptable Manufacturers:

Belimo (Basis of Design)

Siemens

Johnson Controls

* + - * 1. 120 VAC, on/off control, normally closed/fail closed/spring return, full port ball valve, 1 inch size with NPT female ends.
        2. Forged Brass, nickel plated body, stainless steel ball and stem, PTFE seals and lubricated O-ring packing. Rated for minimum 200 PSI at 212°F.
        3. 200 PSI close-off pressure rating, capable of operation at differential pressures up to 30 PSI.
        4. Actuator with visual position indicator, manual hex crank valve over-ride, and conduit fitting for electrical connection.
        5. Valve and actuator shall also comply with the requirements for ball style control valves in Related Section “Mechanical Systems Controls”.
      1. Chemical Feed Pump
         1. Acceptable Manufacturers:

Pulsatron Series E Plus model LPB4 (Basis of Design)

Grundfos

LMI-Flomotion

* + - * 1. Nominal capacity of 1.00 GPH (24 GPD) at 100 PSIG.
        2. 120 VAC/60 HZ/1 PH with minimum 6 foot long three prong grounded plug. UL or ETL approved for indoor and outdoor use.
        3. Reproducibility +/- 2% at maximum capacity.
        4. It shall be possible to manually adjust the stroke rate and stroke length via an adjustment means located on the pump body. Provide the following minimum adjustment ranges:

Stroke rate turn down ratio 10:1

Stroke length turn down ratio 10:1

* + - * 1. It shall also be possible to start and stop the pump via an external mechanical or solid state relay contact.
        2. Provide hand-off-auto switch, circuit protection, and solenoid thermal overload protection with automatic reset.
        3. Pump shall be constructed of glass filled polypropylene (GFPPL), with Teflon diaphragm. Fittings, bleed valve, injection valve, and foot valve shall be GFPPL. Fittings shall accommodate 1/4” to 3/8” I.D. tubing. Provide guided check valves with ceramic balls and Teflon seats and o-rings. With bleed valve for priming.
      1. Bromine Feeder Tank
         1. Acceptable Manufacturers:

Neptune Chemical Pump Company model BT (Basis of Design)

* + - * 1. Vinylester resin body tank, minimum capacity of 20 gallons. 4 inch top opening with threaded, gasketed closure. Two threaded side connections and one threaded bottom connection, all 1 inch NPT. Maximum tank diameter 18 inches.
        2. Tank rated 150 PSI at 150°F.
        3. Provide with accessory piping kit to include inlet diffuser/strainer fitting and exit strainer fitting.

All accessories to be rated 150 PSI at 73°F

All components, including manufacturer, shall comply with the requirements of the related articles in this specification section.

Unions shall have buttress threads.

* + - * 1. All materials shall be compatible with a 20% bromine solution at a pH of 5.0-7.5. All seals shall be Viton, PTFE, or FKM.
      1. Chemical Treatment cONTROLLER with Conductivity probe
         1. Acceptable Manufacturers:

Pulsafeeder “Microvision” model MVS1PB (Basis of Design)

* + - * 1. Multi-function chemical treatment controller for controlling inhibitor feed, biocide feed, and bleed (blow-down). Complete with toroidal conductivity sensor assembly and back-board for mounting of indicated chemical treatment devices. UL, CSA or ETL listed.
        2. Controller features shall include:

Polypropylene enclosure rated NEMA 4X

Pre-wired 15 ft. power cord and pigtails for 115 VAC.

Large LCD display with statistics screen

0–9,999 μS/cm setpoint range

Battery backup

Password protection

Selectable timer

Flow switch to make controller inoperative when no flow is detected. Rated minimum 125 PSIG at 122°F.

Water meter inputs: dry contact and Hall Effect types

Three drum level detection inputs (opened/closed relay type detection)

Dual biocide output relays

Inhibitor output relay

Bleed output relay

Dry contact alarm relay output

All relay outputs rated for 2 amps

Conductivity output: 4-20 mA isolated analog output

PVC back-board for mounting the controller with PVC chemical feed pump shelf attached to the back-board.

* + - * 1. Toroidal sensor assembly features shall include:

No exposed electrodes

Temperature compensated

With in/out ball valves, strainer, injection tee, and rail.

Rated minimum 125 PSI at 122°F

* + - 1. Corrosion Coupon Rack*:*
         1. Acceptable Manufacturers:

Cannon Water Technology

J.L. Wingert

Advantage Controls

Novatech

* + - * 1. 3/4” diameter Schedule 80 PVC coupon rack with two coupon holders, and a 1/4” sample tee with valve. Include inlet/outlet PVC full port ball valves and strainer, and a 0-5 gpm nominal range variable area flow meter (“rotameter”)rated minimum 150 psig at 70°F, with graduated polysulfone or acrylic cylinder, with an accuracy of +/-5%. Provide mild steel and copper coupons.
      1. Solid Corrosion Inhibitor Dissolver
         1. Acceptable Manufacturers:

Solv-Ultima Model 150 (Basis of Design)

Hydro Systems Company Model 590

* + - * 1. Rated for 1.2 GPM minimum, and 100 PSIG at 100°F.
        2. Constructed of chemical resistant parts molded of polypropylene and polyethylene.
        3. Back-up reservoir and float for overflow protection.
        4. Pressure regulator adjustable between 20-40 PSIG.
        5. Pressure gauge and removable filter.
        6. Atmospheric siphon breaker for backflow prevention.
      1. Strainers- clear Plastic
         1. Acceptable Manufacturers:

Spears Manufacturing

Hayward

Nibco

* + - * 1. Clear PVC y-strainer rated 150 PSI at 73°F, with removable basket. With 8 mesh (0.094 inch opening) stainless steel screen.
      1. Flow INDICATORs
         1. Acceptable Manufacturers:

Blue White model F-440 (Basis of Design)

King Instrument

GF Signet

* + - * 1. Variable area flow meter, 0-10 gpm (conductivity loop) 5-21 gpm (brominator loop) nominal range, rated 150 psig at 68°F, with graduated polysulfone or acrylic cylinder, with an accuracy of +/-5%. Rod guided float with stainless steel rod. Provide 3/4 inch pipe size union end connections.
      1. PVC Ball Valves
         1. Acceptable Manufacturers:

Spears Manufacturing

Hayward

Nibco

* + - * 1. True union PVC ball valve rated 200 PSI at 73°F. Full port, PTFE ball seat, peroxide cured EPDM seals, polypropylene handle, buttress threaded union nuts.
        2. Ball valves downstream of the brominator shall be provided with Viton or FKM seals.

Due to the corrosive nature of bromine, the Quill assembly components specified below should not be INDISCRIMINATELY modified. for the same reason, review quill submittal carefully for compliance to the below. Assure all components utilize viton, ptfe, or fkm seals, including unions and ball valves at and downstream of brominator. Check valve PREVENTS back flow during circumstances such as a hose leak.

* + - 1. Retractable Injection quill assembly
         1. Acceptable Manufacturers:

Saf-T-Flo Water Services Inc. EB-159 (Basis of Design)

Hydro Instruments

* + - * 1. Injection quill assembly allowing retraction under pressure consisting of 1-1/2 inch brass stop (ball valve) and compression gland, 1 inch diameter sch. 80 PVC solution tube with 45 degree bevel end, check valve, and 1 inch braided PVC hose assembly. All seals shall be Viton or FKM accept as noted.

All components shall be rated for 150 PSIG working pressure at 100°F. All bromine wetted materials shall be compatible with a 20% bromine solution at a pH of 5.0-7.5.

With 1 inch male inlet connection, 1-1/2 inch male main connection, brass solution tube adapter and packing nut, stainless steel restraint hook, and stainless steel restraint chain. Restraint chain length shall be selected by the manufacturer to allow closure of the stop before withdrawal of the solution tube.

Check valve: Diaphragm style with PVC body, FKM diaphragm, and union nut body. Plast-O-Matic Series CKM. May be provided separate from quill assembly. Mount on solution tube inlet, at downstream end of PVC hose.

Solution tube length shall project into the pipe for a distance equal to 1/3 the diameter of the pipe.

Provide braided PVC hose length adequate to allow solution tube retraction.

Provide stainless steel hose clamps and PVC fittings to allow quill, hose, and pipe connections.

* + - 1. Piping and miscellaneous Components
         1. Provide per Related Sections. For components at or downstream of the brominator, provide with Viton, PTFE, or FKM seals.
      2. chemical solution tubing
         1. Chemical solution tubing for connection to suction and discharge of chemical feed pump and inhibitor dissolver:

Opaque polyethylene tubing rated minimum of 125 PSIG from -50°F to 140°F. Provide polypropylene or stainless steel threaded, compression, or other positive locking style fittings of equivalent rating as required for connection to pump, inhibitor vessel, and rigid piping. Push-on “barbed” style fittings shall not be used.

* + 1. EXECUTION
       1. EXAMINATION AND PREPARATION
          1. Pre-Treatment Conference: Prior to treatment activities, meet with the Project Engineer, Commissioner and contractors to verify treatment procedures, discuss coordination with existing piping networks, and to coordinate treatment activities with construction schedule.
          2. Flush and clean systems per Related Sections and Part 2 above.
          3. Examine roughing-in for equipment support, piping, and electrical connections to verify actual locations, sizes, and other conditions affecting equipment performance, maintenance, and operations. Proceed with installation only after unsatisfactory conditions have been corrected.
       2. INSTALLATION
          1. Install all required components per manufacturer's recommendations and per Related Sections and chemically passivate, treat, and maintain the system per the requirements of Part 2.
          2. Use and dispose of chemicals and wastewater (including from existing piping networks) per the Quality Assurance section of this specification. All costs of disposal shall be borne by the contractor.
          3. Install equipment at locations shown on the Drawings.
          4. Provide all chemicals and all incidental components.
          5. Provide union connections at inlet and outlet to the bromine feed tank.
          6. Make piping connections between dissimilar-metal piping with dielectric fittings per Related Sections.
          7. Provide electrical components in conformance with Related Section.
          8. Provide interconnecting control wiring for chemical treatment controls and sensors per Related Section 230900.
          9. Rigidly support PVC piping at injection quill assembly to prevent pipe movement when operating the isolation valve upstream of the hose connection. Support the quill hose with a hanger that does not abrade the hose surface. Verify that all components at and downstream of the brominator are equipped with the specified seals. Install quill in a location easily accessible for quill removal. Do not mount quill in bottom of pipe. Provide caution label, per detail.
          10. Mount sensors, meters, and all other required components.
          11. Passivate and chemically treat each system immediately after it has been cleaned and flushed.

some projects, such as hospital projects, may desire that water treatment services continue beyond SUBSTANTIAL completion, e.g. a one or more year service contract. contact the u-m design manager for direction, and if needed, Revise the PARAGRAPH below to include that requirement.

* + - * 1. The treatment program shall begin at system start-up or immediately upon first operation of the system by the contractor for temporary use, whichever comes first. Continue the program until Substantial Completion of the system.
      1. FIELD QUALITY CONTROL
         1. The CSP shall:

Verify that systems and equipment have been properly cleaned, flushed, and filled with water, and are fully operational before introducing operational chemicals for water-treatment systems.

Introduce and maintain chemical treatment to achieve the specified performance requirements.

Set-up and program all water treatment control devices. Program water treatment controller to be inoperative when no flow is detected.

Submit a written startup test report for each system placed into service.

Provide validation testing and required reports.

Attend final on-site system turn over meeting with Owner and Commissioner. Present final validation report demonstrating that performance requirements have been achieved and that each system is currently properly treated.

INCLUDE the below ARTICLE IN EVERY SPECIFICATION SECTION.

* + - 1. COMMISSIONING
         1. Perform commissioning activities in accordance with Related Sections.

consult with the u-m design manager to determine if training is desired for your particular project; keep or delete or modify the article below accordingly.

* + - 1. owner TRAINING
         1. CSP shall train Owner's maintenance personnel on equipment operation, adding and maintaining proper chemical levels, trouble-shooting, servicing and preventative maintenance procedures. Do not conduct training until after start up and commissioning is completed. Provide training using documents including the Program Administration Manual and the approved Operations and Maintenance manuals. Provide these documents to the Owner at least two weeks prior to the training to allow sufficient time for review.
         2. Provide 4 hours training minimum.

Schedule training at least 14 days in advance, at date and time approved by Owner.

END OF SECTION 232516